## Slide 1
MMA3001 • BUILDING 60, ROOM G.25
Short-term occupancy forecasting
Can we predict headcount 30 minutes ahead
for ventilation and HVAC planning?
Scope: one room • sensor-derived headcount • May–December 2024
A forecast supports planning; it does not prove energy savings or control HVAC.

## Slide 2
DATA QUALITY
Data audit protects the result
• 643,290 G.25 occupancy events → 23,516 regular 15-minute bins
• Raw headcount range: 0–35 people; median event gap: 4 seconds
• Maximum outage: 21.6 hours. Carry forward limited to 60 minutes; longer gaps remain missing.
• Environmental variables excluded: no validated co-located G.25 mapping.

## Slide 3
METHOD
Leakage-safe forecasting workflow
• Chunk-read the 9-million-row archive, filter the uniquely mapped G.25 floor-space ID.
• Features: current/lagged headcount, rolling history, time of day, weekday and weekend.
• Target: headcount two 15-minute intervals ahead. Future value is excluded from predictors.
• Chronological 60% training / 20% validation / 20% final test; timestamps are never shuffled.

## Slide 4
MODEL COMPARISON
Validation selects the model; testing challenges it
30-minute validation MAE
• Ridge regression: 1.084 people (selected)
• SVR: 1.133 • Decision tree: 1.140
• Persistence: 1.152 • Weekday/time: 1.451
30-minute final-test MAE
• Persistence: 0.461 people
• SVR: 0.509 • Ridge: 0.588
• Decision tree: 0.591 • Weekday/time: 1.168
Ridge was selected before the test. Persistence later won MAE, revealing changed room behaviour.

## Slide 5
HORIZON STUDY
Sensitivity: shorter forecasts are more reliable
Chart: MAE (people)
| 15 min | 30 min | 60 min
Persistence final-test MAE | 0.407 | 0.461 | 0.547
Decision
Use a simple 15-minute persistence baseline for the most accurate tested operational forecast.
Longer horizons increase uncertainty.

## Slide 6
DEMONSTRATION
Repository evidence and responsible next steps
• src/occupancy: documented extraction, features, models, pipeline and sensitivity analysis.
• tests: 5 passing tests; results/test-report.html records verification.
• docs/html: generated source-code documentation; docs/TEST_AND_VIEW.md gives exact commands.
• Limitations: one room, no independent ground truth, long outage, uncertain environmental mapping.
• Next: validate mapping/manual counts and test additional rooms before any control application.
AI use was disclosed; the student must be able to explain every decision and result.